## Slide 1: 50 years of AMD Pollution and Remediation at the Anna S Mine, Tioga County, PA
Robert Hedin
Hedin Environmental
Pittsburgh PA

## Slide 2
Anna S Mine

## Slide 3
Mining and monitoring activities at Anna S Mine | 
Year | Activity
1890s – 1930s | Underground mining, Bloss seam
1976-1986 | Daylighting, Bloss and Cushing seams
1975-76 | Monitoring, Operation Scarlift
1976-1984 | Monitoring, USGS
1985-1989 | Monitoring, Antrim Mining
1996-2000 | Monitoring, PADEP and BCWA
2004-present | Monitoring, BCWA and HE

## Slide 4
 | Period | type | Flow | pH | Acid | Fe | Mn | Al | SO4 | Acid
 |  |  | gpm |  | ----------- mg/L ----------- |  |  |  |  | kg/d
HD | 1975-78 | Pre DL | 438 | 2.8 | 358 | 38 | 4 | na | 475 | 794
HD | 1979-89 | Post DL |  |  |  |  |  |  |  | 
HD | 1995-98 | Pre PTS |  |  |  |  |  |  |  | 
HD | 2004-18 | PTS |  |  |  |  |  |  |  | 
S1 | 1975-78 | Pre DL | 436 | 3.0 | 218 | 13 | 4 | na | 340 | 516
S1 | 1979-89 | Post DL |  |  |  |  |  |  |  | 
S1 | 1995-98 | Pre PTS |  |  |  |  |  |  |  | 
S1 | 2004-18 | PTS |  |  |  |  |  |  |  | 
S2 | 1975-76 | Pre DL | 39 | 3.8 | 39 | <1 | na | na | 96 | 8
S2 | 1980-91 | Post DL |  |  |  |  |  |  |  | 
S2 | 1995-98 | Pre PTS |  |  |  |  |  |  |  | 
S2 | 2004-18 | PTS |  |  |  |  |  |  |  | 

## Slide 7: Daylighting / Remining
Removal of stumps from deep mine
Mining of Cushing coal seam above the mine
Existing deep mine discharges avoided
Overburden net acidic
No alkaline addition (pre-ABA requirements)

## Slide 8
Chart: HD acidity, 1975 - 2018
remining begin | 2500 | 0
remining end | 2500 | 0
constructon | 2500 | 0
Daylighting starts
Daylighting ends
Passive Systems installed

## Slide 9
Chart: HD flow, 1975 - 2018
| 37986 | 37986
constructon | 1200 | 0
remining begin | 1200 | 0
remining end | 1200 | 0

## Slide 10
 | Period | type | Flow | pH | Acid | Fe | Mn | Al | SO4 | Acid
 |  |  | gpm |  | ----------- mg/L ----------- |  |  |  |  | kg/d
HD | 1975-78 | Pre DL | 438 | 2.8 | 358 | 38 | 4 | na | 475 | 794
HD | 1979-89 | Post DL | 282 | 2.7 | 1000 | 112 | 24 | 74 | 715 | 1361
HD |  |  |  |  |  |  |  |  |  | 
HD |  |  |  |  |  |  |  |  |  | 
S1 | 1975-78 | Pre DL | 436 | 3.0 | 218 | 13 | 4 | na | 340 | 516
S1 | 1979-89 | Post DL | 219 | 2.9 | 480 | 38 | 18 | 33 | 704 | 583
S1 |  |  |  |  |  |  |  |  |  | 
S1 |  |  |  |  |  |  |  |  |  | 
S2 | 1975-76 | Pre DL | 39 | 3.8 | 39 | <1 | na | na | 96 | 8
S2 | 1980-91 | Post DL | 28 | 3.0 | 294 | 20 | 21 | 15 | 639 | 47
S2 |  |  |  |  |  |  |  |  |  | 
S2 |  |  |  |  |  |  |  |  |  | 

## Slide 11: Consequences of Increased AMD
Severely polluted 6 miles of Babb Creek
Degraded 5 miles of Pine Creek downstream of Babb
1990: Fish Commission found no fish in Babb Creek below Wilson
1990: Babb Creek Watershed Association formed
1996: Babb Creek placed on 303(d) list
1996: Antrim Mining builds lime treatment plant for Antrim discharges
1996: Push to install treatment on Anna S discharges

## Slide 12
Chart: HD acidity, 1975 - 2018
remining begin | 2500 | 0
remining end | 2500 | 0
constructon | 2500 | 0
Daylighting starts
Daylighting ends
Passive Systems installed

## Slide 13
 | Period | type | Flow | pH | Acid | Fe | Mn | Al | SO4 | Acid
 |  |  | gpm |  | ----------- mg/L ----------- |  |  |  |  | kg/d
HD | 1975-78 | Pre DL | 438 | 2.8 | 358 | 38 | 4 | na | 475 | 794
HD | 1979-89 | Post DL | 282 | 2.7 | 1000 | 112 | 24 | 74 | 715 | 1361
HD | 1995-98 | Pre PTS | 311 | 2.8 | 491 | 44 | 10 | 36 | 715 | 845
HD | 2004-18 | PTS |  |  |  |  |  |  |  | 
S1 | 1975-78 | Pre DL | 436 | 3.0 | 218 | 13 | 4 | na | 340 | 516
S1 | 1979-89 | Post DL | 219 | 2.9 | 480 | 38 | 18 | 33 | 704 | 583
S1 | 1995-98 | Pre PTS | 278 | 3.0 | 271 | 12 | 14 | 16 | 542 | 425
S1 | 2004-18 | PTS |  |  |  |  |  |  |  | 
S2 | 1975-76 | Pre DL | 39 | 3.8 | 39 | <1 | na | na | 96 | 8
S2 | 1980-91 | Post DL | 28 | 3.0 | 294 | 20 | 21 | 15 | 639 | 47
S2 | 1995-98 | Pre PTS | 58 | 3.2 | 140 | 2 | 8 | 7 | 286 | 60
S2 | 2004-18 | PTS |  |  |  |  |  |  |  | 

## Slide 14
Anoxic Limestone Drain
Ponds
Vertical Flow Pond
Oxic Limestone Bed
Wetland
Ponds
Ponds
Oxic Limestone Bed (drainable)
Net
Alkaline
Net alkaline
Net acid
Net acid
DO, Fe3+, Al all < 1 mg/L
(high Fe2+)
Characterize Mine Water
Wetland
Final Discharge
Mn
DO, Fe3+, Al any > 1 mg/L
DO, Fe3+, Al any > 1 mg/L
Fe < 10 mg/L
High Fe2+
Ponds
Repeat As Needed
Mn

## Slide 17: General Site Layout
Anna S1
Anna S2
Hunter’s Drift
VFP2
VFP4
VFP3
VFP1
Anna VFPs
VFP6
VFP7
VFP8
VFP5
Hunter’s VFPs
Wetland 1
Wetland 2
Wetland 3
Wetland 4
Treated water to stream

## Slide 19
Largest project undertaken by citizen group in PA
$2.5 million (2002) in state, federal, and private funds
Three pipelines totaling 8,000 ft of pipe
8 vertical flow ponds covering 7 acres
  39,000 tons of limestone
  6,500 cubic yards of compost
4 constructed wetlands covering 4 acres
Anna S Mine Complex Passive System

## Slide 21
 | Period | type | Flow | pH | Acid | Fe | Mn | Al | SO4 | Acid
 |  |  | gpm |  | ----------- mg/L ----------- |  |  |  |  | kg/d
HD | 1975-78 | Pre DL | 438 | 2.8 | 358 | 38 | 4 | na | 475 | 794
HD | 1979-89 | Post DL | 282 | 2.7 | 1000 | 112 | 24 | 74 | 715 | 1361
HD | 1995-98 | Pre PTS | 320 | 2.8 | 491 | 44 | 10 | 36 | 715 | 845
HD | 2004-18 | PTS |  | 2.8 | 335 | 33 | 6 | 31 | 545 | 396
S1 | 1975-78 | Pre DL | 436 | 3.0 | 218 | 13 | 4 | na | 340 | 516
S1 | 1979-89 | Post DL | 219 | 2.9 | 480 | 38 | 18 | 33 | 704 | 583
S1 | 1995-98 | Pre PTS | 278 | 3.0 | 271 | 12 | 14 | 16 | 542 | 425
S1 | 2004-18 | PTS |  | 3.1 | 136 | 7 | 8 | 12 | 339 | 125
S2 | 1975-76 | Pre DL | 39 | 3.8 | 39 | <1 | na | na | 96 | 8
S2 | 1980-91 | Post DL | 28 | 3.0 | 294 | 20 | 21 | 15 | 639 | 47
S2 | 1995-98 | Pre PTS | 58 | 3.2 | 140 | 2 | 8 | 7 | 286 | 60
S2 | 2004-18 | PTS |  | 3.8 | 29 | 1 | 5 | 2 | 125 | 5

## Slide 22
Average flow and chemistry for Anna and HD treatment systems, 2004 – 2019 |  |  |  |  |  |  |  | 
Point | Flow | pH | Alk | Acid | Fe | Al | Mn | SO4
 | gpm |  | mg/L CaCO3 |  | mg/L | mg/L | mg/L | mg/L
Anna System |  |  |  |  |  |  |  | 
S1 & S2 in | 206 | 3.1 | 0 | 123 | 6.0 | 10.9 | 7.4 | 314
VFPs out | na | 7.0 | 157 | -123 | 5.6 | 0.5 | 6.5 | 310
Final | na | 7.5 | 134 | -108 | 1.1 | 0.3 | 3.2 | 302
Hunters Drift System |  |  |  |  |  |  |  | 
HD in | 243 | 2.8 | 0 | 335 | 33.3 | 31.4 | 6.1 | 545
VFPs out | na | 6.8 | 194 | -130 | 17.8 | 0.5 | 5.2 | 521
Final | na | 7.5 | 141 | -114 | 0.5 | 0.2 | 1.9 | 480

## Slide 23
Chart: Hunters Drift System Final Effluent
| 38153 | 38262 | 38264 | 38288 | 38318 | 38350 | 38410 | 38432 | 38464 | 38484 | 38663 | 38966 | 39050 | 39196 | 39288 | 39413 | 39428 | 39503 | 39518 | 39629 | 39668 | 39679 | 39724 | 39752 | 39790 | 39889 | 40057 | 40169 | 40194 | 40227 | 40254 | 40288 | 40345 | 40434 | 40582 | 40624 | 40652 | 40724 | 40806 | 41163 | 41221 | 41221 | 41222 | 41241 | 41263 | 41340 | 41358 | 41410 | 41521 | 41521 | 41548 | 41549 | 41577 | 41709 | 41738 | 41954 | 42063 | 42130 | 42170 | 42304 | 42328 | 42130 | 42450 | 42509 | 42597 | 42621 | 42653 | 42696 | 42768 | 42813 | 42859 | 43002 | 43070 | 43173 | 43332 | 43369 | 43549 | 43585
 | -145 | -109 | -134 | -139 | -131 | -98 | -115 | -145 | -87 | -79 | -94 | -79 | -86 | -59.49 | -119.78 | -134 | -101 | -127 | -150 | -142 | -101.53 | -94 | -100 | -82 | -131 | -122 | -93 | -105 | -74 | -83 | -78 | -104 | -137 | -112 | -107 | -99 | -133 | -186 | -169 | -119.58 | -126.48 | -139.8 | -113 | -90 | -110.25 | -117 | -113.15 | -138.01 | -92 | -113.32 | -84 | -126 | -148 | -134.13 | -135 | -125 | -102 | -114 | -101 | -90

## Slide 24
Chart: Anna System Final Effluent
| 38153 | 38262 | 38264 | 38288 | 38318 | 38350 | 38410 | 38432 | 38465 | 38484 | 38663 | 38966 | 39050 | 39196 | 39413 | 39518 | 39629 | 39679 | 39790 | 39889 | 40057 | 40194 | 40227 | 40254 | 40288 | 40434 | 40582 | 40624 | 40724 | 40806 | 41163 | 41241 | 41340 | 41358 | 41410 | 41548 | 41709 | 41738 | 41954 | 42170 | 42304 | 42328 | 42130 | 42536 | 42450 | 42509 | 42597 | 42597 | 42697 | 42768 | 42813 | 42859 | 43002 | 43070 | 43173 | 43332 | 43369 | 43549 | 43585
 | -181 | -69 | -62 | -104 | -83 | -69 | -75 | -102 | -106 | -79.98 | -103 | -121 | -119 | -111 | -118.97 | -99 | -95.24 | -116 | -111.6 | -119 | -76.81 | -119.2 | -64 | -83.43 | -95 | -79.6 | -109 | -72.32 | -53.45 | -57 | -59.9 | -68 | -51.79 | -57 | -80.59 | -62 | -505 | -169 | -125.37 | -154 | -222.8 | -114 | -113 | -113 | -153 | -80

## Slide 25: Maintenance of the Systems
Routine Maintenance
Babb Creek Watershed Association
Monthly inspections; semi-annual sampling; simple maintenance
$10,711 in 2018
Major Maintenance
Activities that require fund raising and outside contracting
Replacement of organic substrates, repairs to collection structures; access road improvements

## Slide 26: Substrate Investigation

## Slide 27: Substrate Investigation, Good Result

## Slide 28: Substrate Investigation, Bad Result

## Slide 29: Organic Substrate Rehab Process
Isolate VFP
Strip off existing substrate
scarify limestone aggregate
Place 9-12” of new alkaline substrate
replace old substrate on top

## Slide 31: Organic Substrate Rehabilitation
Hunters Drift VFP Rehab
VFP8 in 2012
VFP5, VFP6, VFP7 in 2013
$210,008
Anna VFP Rehab
VFP1, VFP2, VFP3, VFP4 in 2016
$201,706

## Slide 32
Water Quality Impacts of Mining and Treatment | 
Year | Activity
1890s – 1930s | Underground mining, Bloss seam
1975-76 | Monitoring, Operation Scarlift
1976-1986 | Daylighting, Bloss and Cushing seams
1976-1984 | Monitoring, USGS
1985-1989 | Monitoring, Antrim Mining
1996 | Babb Creek placed on 303(d) list
1996-2000 | Monitoring, PADEP and BCWA
2003-2004 | Construction of treatment system
2004-present | Monitoring, BCWA and HE
2010 | Babb Creek removed from 303(d) list Sections of Babb Creek designated as Wild Trout stream
2012-2013 | Hunters Drift organic substrate replacement
2016 | Anna organic substrate replacement

## Slide 33: Looking Forward
Deep mines will continue to discharge low pH Al and Fe contaminated mine water
Continued operation of the passive treatment systems will be required to maintain Babb Creek as a cold water fishery
Long-term O&M commitment includes
  Routine maintenance by BCWA
  Major maintenance (organic substrate rehab) every 10-25 years

## Slide 34: Questions / Comments