## Slide 1: Passive removal of Mn from mine water by heterogeneous Mn oxidation
Robert Hedin, Neil Wolfe, Benjamin Hedin
Hedin Environmental, Pittsburgh PA
American Society of Reclamation Sciences
39th Annual Conference, Duluth MN
June 12-16, 2022

## Slide 2: Manganese: origin
Acid dissolution of carbonate or silicate minerals
Reduction of Mn oxides

## Slide 3: Mn: why is it regulated?
  Surrogate for other more hazardous metals (Kleinmann papers in the 1980s)
  Ecotoxicity at high instream concentrations
  “…At levels beyond those necessary to maintain adequate health, manganese has been identified as a nervous system toxin and has been specifically linked to negative impacts on fetal and childhood neurodevelopment.” (Pennsylvania Environmental Quality Board, Water Quality Standard for Manganese and Implementation, July 25, 2020)

## Slide 4: Mn: effluent standards
SMCRA and most US mining programs
  2.0 mg/L monthly average
International hardrock mining sites
  0.5 mg/L
Proposed Pennsylvania standard
  0.3 mg/L

## Slide 5: Mn: treatment
Potential solids
MnS (rare), MnCO3 (uncommon), MnOOH (unstable)
MnO2 (common)
pyrolusite, birnessite

## Slide 6: MnO2 formation
oxidation Mn2+ + ½O2 + 2H+  Mn4+ + H2O
hydrolysis Mn4+ + 2H2O  MnO2 + 4H+
Sum Mn2+ + ½O2 +H2O  MnO2 + 2H+
hydrolysis is very rapid
oxidation is limiting step

## Slide 7: Mn2+ oxidation kineticsA
At contant pH and dissolved O2:
d[Mn2+]/dt = -k0[Mn2+] – k1[Mn2+] [MnO2]
k0 and k1 are rate constants
[MnO2] is surface area of Mn solids
A Based on Stumm and Morgan (1996); Rose, Means and Shah (2003); Means and Rose (2005)

## Slide 8: Homogeneous oxidation mechanism
d[Mn2+]/dt = -k0[Mn2+] – k1[Mn2+] [MnO2]
Strongly pH dependent and requires pH >9
NaOH is commonly used in conventional treatment
Over-treatment will result in effluent pH >10 and formation of Mg solids
Many states provide high-pH waivers for NaOH treatment systems

## Slide 9: Heterogeneous oxidation mechanism
d[Mn2+]/dt = -k0[Mn2+] – k1[Mn2+] [MnO2]
Sorption of Mn2+ to solids, where oxidation can occur much more rapidly at lower pH
Means and Rose suggest that surface area of [MnO2] is rate-limiting factor
Appropriate solids
  Wetland substrate
  Organic substrates (coconut coir)
  Inorganic substrates (carpet fibers)
  Mineral substrates (aggregate)
Microbial or fungal contribution

## Slide 10: Requirements for heterogeneous Mn removal
Aerobic conditions (1 mg/L Mn  0.3 mg/L O2)
Low Fe2+
Substrate for MnO2 accumulation: aggregate
  carbonate aggregate if water has low pH
  no preference is water has circumneutral pH
Development of enough MnO2 to promote the heterogeneous reaction
Retention times vary with concentration and substrate size

## Slide 11: the right stuff

## Slide 12: Case Studies Unexpected Mn removal by aggregate systems

## Slide 13: Mitchell limestone flushing project 2006-2008
30 CY roll off containers filled with limestone
AgriDrain
Smart Drainage System

## Slide 14: Mitchell West Box, 2008-2020
 | pH | Alk | Acid | Mn | Fe | Al | SO4
 | s.u. | mg/L CaCO3 |  | mg/L | mg/L | mg/L | mg/L
Influent | 3.0 | 0 | 200 | 11.9 | 6.8 | 21.5 | 523
effluent | 6.9 | 82 | -61 | 2.8 | 0.5 | 3.4 | 495

## Slide 15: West Box (Tioga County, Pennsylvania)
Chart: Mn mg/L
| 39734 | 39737 | 39745 | 39764 | 39790 | 39895 | 39986 | 40067 | 40169 | 40194 | 40227 | 40254 | 40288 | 40324 | 40345 | 40388 | 40477 | 40582 | 40624 | 40724 | 40806 | 40840 | 40869 | 40998 | 41144 | 41171 | 41183 | 41241 | 41263 | 41340 | 41410 | 41481 | 41549 | 41577 | 41709 | 41856 | 42251 | 42063 | 42170 | 42328 | 42509 | 42621 | 42653 | 42697 | 42769 | 43070 | 43173 | 43585 | 43873
influent | 17.74 | 17.94 | 18.15 | 16.75 | 19.89 | 11.3 | 11.89 | 12.94 | 14.82 | 12.76 | 12.72 | 13 | 7.45 | 12.14 | 11.83 | 12.2 | 15.3 | 10.79 | 9.53 | 10.99 | 13.62 | 8.69 | 10.87 | 11.79 | 11.55 | 14.01 | 13.4 | 12.92 | 9.93 | 9.05 | 14.2 | 11.7 | 9.2 | 10.17 | 9.5 | 11.17 | 8.7 | 10.33 | 10.9 | 10.6 | 7.25 | 7.4 | 6.29
effluent | 1.52 | 2.76 | 1 | 1.46 | 3.72 | 1.36 | 2.35 | 0.72 | 0.02 | 3.98 | 3.69 | 7.23 | 3.2 | 5.7 | 2.85 | 2.84 | 3.19 | 1.99 | 6.93 | 2.93 | 1.35 | 0.69 | 5.81 | 2.5 | 0.81 | 4.73 | 9 | 1.09 | 2.58 | 2.85 | 5.5 | 3.75 | 2.2 | 3.08 | 3.37 | 5.2 | 1.28 | 6.76 | 2.3 | 0.75 | 3.2 | 0.69 | 0.5 | 0.1 | 0.32 | 0.05 | 0.05
SDS vandalized | 25 | 0

## Slide 16: West Box (Tioga County, Pennsylvania)
Chart: Mn mg/L
| 39734 | 39737 | 39745 | 39764 | 39790 | 39895 | 39986 | 40067 | 40169 | 40194 | 40227 | 40254 | 40288 | 40324 | 40345 | 40388 | 40477 | 40582 | 40624 | 40724 | 40806 | 40840 | 40869 | 40998 | 41144 | 41171 | 41183 | 41241 | 41263 | 41340 | 41410 | 41481 | 41549 | 41577 | 41709 | 41856 | 42251 | 42063 | 42170 | 42328 | 42509 | 42621 | 42653 | 42697 | 42769 | 43070 | 43173 | 43585 | 43873
influent | 17.74 | 17.94 | 18.15 | 16.75 | 19.89 | 11.3 | 11.89 | 12.94 | 14.82 | 12.76 | 12.72 | 13 | 7.45 | 12.14 | 11.83 | 12.2 | 15.3 | 10.79 | 9.53 | 10.99 | 13.62 | 8.69 | 10.87 | 11.79 | 11.55 | 14.01 | 13.4 | 12.92 | 9.93 | 9.05 | 14.2 | 11.7 | 9.2 | 10.17 | 9.5 | 11.17 | 8.7 | 10.33 | 10.9 | 10.6 | 7.25 | 7.4 | 6.29
effluent | 1.52 | 2.76 | 1 | 1.46 | 3.72 | 1.36 | 2.35 | 0.72 | 0.02 | 3.98 | 3.69 | 7.23 | 3.2 | 5.7 | 2.85 | 2.84 | 3.19 | 1.99 | 6.93 | 2.93 | 1.35 | 0.69 | 5.81 | 2.5 | 0.81 | 4.73 | 9 | 1.09 | 2.58 | 2.85 | 5.5 | 3.75 | 2.2 | 3.08 | 3.37 | 5.2 | 1.28 | 6.76 | 2.3 | 0.75 | 3.2 | 0.69 | 0.5 | 0.1 | 0.32 | 0.05 | 0.05
SDS vandalized | 25 | 0
Effluent percentile
Concentrations
90th 5.8 mg/L
75th 3.7 mg/L
50th 2.7 mg/L
25th 1.0 mg/L
10th 0.4 mg/L

## Slide 17: Scootac #1

## Slide 18: Scootac #1, 2010-2020
 | pH | Alk | Acid | Mn | Fe | Al | SO4
 | s.u. | mg/L CaCO3 |  | mg/L | mg/L | mg/L | mg/L
Influent | 4.0 | 0 | 86 | 23.5 | 0.2 | 10.3 | 889
effluent | 7.3 | 189 | -162 | 1.6 | 0.1 | 0.2 | 914

## Slide 19: Scootac #1, (Clinton County, Pennsylvania)
Chart: Mn, mg/L
| 40501 | 40541 | 40560 | 40597 | 40619 | 40652 | 40681 | 40721 | 40743 | 40786 | 40815 | 40837 | 40863 | 40891 | 40938 | 40963 | 40991 | 41032 | 41073 | 41120 | 41191 | 41261 | 41512 | 41641 | 41698 | 41724 | 41746 | 42640 | 42836 | 43018 | 43048 | 43389 | 43566 | 43787 | 43949
Influent | 33.36 | 26.6 | 28.42 | 28.19 | 17.69 | 20.77 | 24.85 | 31.24 | 37.09 | 35.45 | 27.26 | 25.04 | 25.9 | 24.05 | 24.66 | 27.02 | 26.69 | 29.1 | 24.66 | 25.55 | 32.42 | 15.99 | 33.35 | 15.86 | 19.58 | 19.8 | 16.81 | 20.44 | 12.32 | 17.33 | 12.4 | 10.49 | 10.7 | 11.1
LS effluent | 22.41 | 1.42 | 0.23 | 1.65 | 0.3 | 1.36 | 0.65 | 1.04 | 1.08 | 0.08 | 0.09 | 0.28 | 0.02 | 0.33 | 0.53 | 0.27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.05 | 5.09 | 1.07 | 3.43 | 4.53 | 7.76 | 0.02 | 0.02 | 0.4 | 0.06 | 0.9 | 0.02
limestone cleaned | 200 | -300
 | 200 | -300

## Slide 20: Scootac #1, (Clinton County, Pennsylvania)
Chart: Mn, mg/L
| 40501 | 40541 | 40560 | 40597 | 40619 | 40652 | 40681 | 40721 | 40743 | 40786 | 40815 | 40837 | 40863 | 40891 | 40938 | 40963 | 40991 | 41032 | 41073 | 41120 | 41191 | 41261 | 41512 | 41641 | 41698 | 41724 | 41746 | 42640 | 42836 | 43018 | 43048 | 43389 | 43566 | 43787 | 43949
Influent | 33.36 | 26.6 | 28.42 | 28.19 | 17.69 | 20.77 | 24.85 | 31.24 | 37.09 | 35.45 | 27.26 | 25.04 | 25.9 | 24.05 | 24.66 | 27.02 | 26.69 | 29.1 | 24.66 | 25.55 | 32.42 | 15.99 | 33.35 | 15.86 | 19.58 | 19.8 | 16.81 | 20.44 | 12.32 | 17.33 | 12.4 | 10.49 | 10.7 | 11.1
LS effluent | 22.41 | 1.42 | 0.23 | 1.65 | 0.3 | 1.36 | 0.65 | 1.04 | 1.08 | 0.08 | 0.09 | 0.28 | 0.02 | 0.33 | 0.53 | 0.27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.05 | 5.09 | 1.07 | 3.43 | 4.53 | 7.76 | 0.02 | 0.02 | 0.4 | 0.06 | 0.9 | 0.02
limestone cleaned | 200 | -300
 | 200 | -300

## Slide 21: Case Studies Targeted Mn removal by aggregate systems

## Slide 22: Phu Kham copper mine (Laos)

## Slide 23: Phu Kham, 2013-2020
 | pH | Alk | Acid | Mn | Fe | Al | SO4
 | s.u. | mg/L CaCO3 |  | mg/L | mg/L | mg/L | mg/L
Influent | 6.9 | 250 | na | 3.0 | 0.2 | <0.1 | 427
effluent | 7.2 | 251 | na | <0.1 | <0.1 | <0.1 | 466

## Slide 24: Phu Kham (Lao People’s Democratic Republic)
Chart: Mn, mg/L

## Slide 25: Phu Kham (Lao People’s Democratic Republic)
Chart: Mn, mg/L

## Slide 26: Tenmile

## Slide 27: Tenmile, 2015-2022
 | pH | Alk | Acid | Mn | Fe | Al | SO4
 | s.u. | mg/L CaCO3 |  | mg/L | mg/L | mg/L | mg/L
Influent | 3.2 | 0 | 146 | 30.8 | 2.7 | 3.1 | 1710
effluent | 7.7 | 105 | -59 | 1.1 | 0.8 | 0.1 | 1888

## Slide 28: Tenmile (Greene County, Pennsylvania)
Chart: Mn, mg/L
| 42066 | 42072 | 42081 | 42087 | 42096 | 42102 | 42108 | 42136 | 42136 | 42173 | 42215 | 42311 | 42459 | 42530 | 42760 | 42952 | 43098 | 43184 | 43187 | 43257 | 43479 | 43543 | 43600 | 43675 | 43694 | 43697 | 44137 | 44404
Influent | 21.9 | 22.8 | 26.4 | 29.8 | 27 | 22.2 | 33.8 | 29.992 | 37.8 | 37.2 | 32 | 28.2 | 35 | 18.45 | 33.95 | 40.3 | 35.4 | 34.6 | 35.4 | 25.4 | 27.6 | 32.25 | 31.25 | 29.4 | 27.8 | 25.4 | 23.2
LS addition | 50 | 0
 | 50 | 0
 | 50 | 0

## Slide 29: Tenmile (Greene County, Pennsylvania)
Chart: Mn, mg/L
LS addition | 50 | 0
 | 50 | 0
 | 50 | 0

## Slide 30: Conclusions
Passive removal of Mn at circumneutral pH is feasible
Treatment requires MnO2-coated substrate that promotes the heterogeneous oxidation mechanism
The buildup of sufficient reactive solids takes 4-8 weeks
Very low effluent concentrations are possible
Periodic maintenance of the treatment bed is necessary to maintain treatment

## Slide 31: Questions?
Too much of the right stuff

## Slide 33: Hedin Environmental is Hiring!!!
Diverse mine drainage and passive treatment projects
Field and design/engineering openings
Competitive pay and benefits
Pennsylvania is a happening place
Talk to Bob Hedin or email Ben Hedin, ben.hedin@hedinenv.com
The future is so bright, we have to wear shades

## Slide 34
If other metals are involved, Mn removal is delayed