## Slide 1: Evaluation of Peat Sorption Media for Metal Removal from Stormwater from a Mineral Processing Facility
Candace Kairies-Beatty, Alex Vaslow,
Caleb Robb, Luke Zwiefelhofer
Winona State University
Paul Eger Talon Metals Peggy Jones, Doug Green American Peat Technology

## Slide 2: Overview
Peat based sorption media
The Site
Column Testing
  Column design
  Operational issues
  Results
Biochar Comparison
Conclusions

## Slide 3: What is Peat based sorption media?
APTsorb /APTivator TM
  Patented peat based sorption media
  Hardened granule
APTsorb TM Granule

## Slide 4: Why should I care?
  Large surface area
  High hydraulic conductivity (~0.5 cm/sec)
  High metal affinity (1-15% max dry wgt)
  Can remove particulates < 5-10 microns
APTsorb TM Granule 1500x

## Slide 5: The Site
Metal processing facility
Industrial stormwater
pH ~ 7-8
Elevated Pb, Zn, Cd
 | Cadmium (ug/L) | Lead (ug/L) | Zinc (ug/L)
Stormwater | 112 | 615 | 8361
Permit Limit | 0.5 | 7.9 | 72.5
Flow 160 gpm

## Slide 6: The Problem
Aging treatment system
Requiring 24/7 supervision

## Slide 7: Objectives
Can peat sorption media treat this water?
Is there a difference between peat media?
Compare peat media to biochar

## Slide 8
Frit
Frit
Frit
Glass wool
Glass beads
Media
2 5/8
3/16
1/8
1/8
1/8
1/2
72 grams peat media
in
Flow 20 ml/min
Contact time 7.5 min
Schematic not to scale
Approach

## Slide 9: Column Test 1
APTsorb

## Slide 11
Zinc

## Slide 12
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 0 | 11 | 20 | 23 | 32 | 38 | 43 | 76 | 109 | 120 | 250 | 400 | 866 | 1681 | 2349 | 2930 | 3435
Permit Limit

## Slide 13
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 0.05 | 0.08 | 0.12 | 0.72 | 0.574 | 1.159 | 1.679 | 3.01 | 7.95 | 16.11 | 24.25 | 33.58 | 37.76
Cadmium

## Slide 14
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 1.24 | 1.64 | 1.45 | 1.97 | 1.903 | 1.754 | 1.574 | 0.556 | 0.567 | 0.496 | 0.364 | 0.481 | 0.513
Pb

## Slide 15
Chart: Zinc mass per Layer of Media
| A | B | C | D
Zn | 196291.4286 | 246029.4071 | 291227.393 | 356377.6744

## Slide 16
Chart: Metals mass per Layer of Media
| A | B | C | D
Cd | 3016.5714 | 5167.4941 | 8329.8677 | 12344.093
Cu | 128.5714 | 200.6324 | 366.3035 | 501.6279
Pb | 238.0714 | 990.5692 | 4932.3502 | 23436.4884

## Slide 17: Media Digestion
Column section | Section | Zn ug | Cd ug | Pb ug
A | Top | 10905 | 168 | 13
B |  | 13668 | 287 | 55
C |  | 16179 | 463 | 274
D | Bottom | 19799 | 686 | 1302
Solids mg/kg | Average | 15138 | 401 | 411
Total mass |  | 1,089,926 | 28,858 | 29,597

## Slide 18: Media Digestion
Column section | Section | Zn ug | Cd ug | Pb ug
A | Top | 10905 | 168 | 13
B |  | 13668 | 287 | 55
C |  | 16179 | 463 | 274
D | Bottom | 19799 | 686 | 1302
 |  | 15138 | 401 | 411
Total mass |  | 1,089,926 | 28,858 | 29,597
mass water |  | 1,037,431 | 32,167 | 25,416
% difference |  | 5% | -9% | 12%

## Slide 19: Column Test 2
APTivator

## Slide 21
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 0 | 11 | 20 | 23 | 32 | 38 | 43 | 76 | 109 | 120 | 250 | 400 | 866 | 1681 | 2349 | 2930 | 3435
Run 2 APTivator | 0 | 10 | 28 | 50 | 77 | 98 | 219 | 375 | 1130 | 2176 | 2670 | 3035
Average influent Zn concentration | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235

## Slide 24: Column Test 3
APTivator

## Slide 26
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 0 | 11 | 20 | 23 | 32 | 38 | 43 | 76 | 109 | 120 | 250 | 400 | 866 | 1681 | 2349 | 2930 | 3435
Run 2 APTivator | 0 | 10 | 28 | 50 | 77 | 98 | 219 | 375 | 1130 | 2176 | 2670 | 3035
Run 3 APTivator | 4 | 30 | 51 | 62 | 83 | 91 | 47 | 65 | 108 | 98 | 160 | 152 | 633 | 1090 | 1540 | 1900
Average influent Zn concentration | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235

## Slide 27: Column Test 4
Biochar

## Slide 28: Biochar
Charcoal-like substance
Burn organic material in a controlled process
Biochar Solutions

## Slide 29
Column
14 grams

## Slide 31
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 108 | 120 | 144 | 168
Run 4 Biochar | 4 | 10 | 24 | 45 | 72 | 113 | 278 | 563 | 1272 | 1507 | 1610 | 1975 | 1957 | 5958 | 6471 | 6595 | 6446
Average influent Zn concentration before spike | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235 | 6235
Average influent Zn concentration with spike | 4268 | 4268 | 4268 | 4268

## Slide 32
Chart: Elapsed Time (hours)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 9 | 12 | 24 | 36 | 48 | 72 | 96 | 120 | 144 | 168
Run 1 APTSorb | 0 | 11 | 20 | 23 | 32 | 38 | 43 | 76 | 109 | 120 | 250 | 400 | 866 | 1681 | 2349 | 2930 | 3435
Run 2 APTivator | 0 | 10 | 28 | 50 | 77 | 98 | 219 | 375 | 1130 | 2176 | 2670 | 3035
Run 3 APTivator | 4 | 30 | 51 | 62 | 83 | 91 | 47 | 65 | 108 | 98 | 160 | 152 | 633 | 1090 | 1540 | 1900
Run 4 Biochar | 4 | 10 | 24 | 45 | 72 | 113 | 278 | 563 | 1272 | 1507 | 1610 | 1975 | 1957 | 5958 | 6471 | 6595 | 6446

## Slide 33
Chart: Zinc Concentration in Column Media
| A | B | C | D
Biochar | 4452 | 4995.7082 | 6031.0794 | 6312.3467
APTSorb | 10905.0794 | 13668.3004 | 16179.2996 | 19798.7597

## Slide 34: Conclusion
All products remove metals from water
Would require lead/lag approach
Better removal with peat

## Slide 35
Looking for Answers?
Ask a question!
Thank you!