## Slide 1: Gladden AMD Treatment Plant
Chartiers Creek Watershed
South Fayette Township
Allegheny County
Pennsylvania

## Slide 2: The Gladden AMD Treatment Facility
South Fayette Conservation Group (SFCG) received a $13,048,446 AML Economic Revitalization (AML Pilot) Grant from the PA DEP Bureau of Abandoned Mine Reclamation in 2019.
SFCG contracted with Tetra Tech to complete a Design-Build Project to design and build the Gladden AMD Treatment Facility.
The Gladden mine drainage treatment plant, located just west of Pittsburgh Pennsylvania in the Chartiers Creek watershed, South Fayette Township, Allegheny County, represents a mutli-decades effort to address and ameliorate the impacts of abandoned underground coal mine drainage in the local community.

## Slide 3: South Fayette Conservation Group
The South Fayette Conservation Group (SFCG) is a non-profit conservation and watershed group located in southern Allegheny County about 12 miles southwest of Pittsburgh. Their mission is to conserve, protect and enhance our natural and recreational resources for the benefit of their families and neighbors.
The SFCG addresses conservation issues associated with urban growth and abandoned mine drainage (AMD), which impacts major tributaries in the region including Millers Run, Coal Run, Fishing Run, Robinson Run and Chartiers Creek. In addition, the group seeks to increase public awareness of these issues and to increase involvement among different sectors of their community.
SFCG is a volunteer organization that partners with private, local and state organizations to complete special projects including but are not limited to abandoned mine drainage reclamation, major stream remediation, riparian land restorations and several community and education outreach initiatives among many other achievements.

## Slide 4: Gladden Project History
2003 PaDEP Growing Greener grant develop Lower Chartiers Creek Watershed Restoration Plan
2005 - Restoration Plan for Large Mine Discharges to Lower Chartiers Creek determines Gladden discharge to be largest point source in the watershed - Tom Gray, Engr. Mgr.
2006 Grant from Growing Greener II for the Fishing Run Restoration/Maude Mine Reclamation Project completed in 2007.
2009 Growing Greener Grant Recipient for the South Fayette Watershed Visual Assessment including Millers Run
2009 Clean Water Fund Grant Program Recipient sponsored by the Allegheny County Conservation District for our Fish Habitat Project for Millers Run completed in 2011

## Slide 5: Gladden Project History (continued)
May 9, 2019 – South Fayette Conservation Group (SFCG) AML PILOT Grant Application Submitted
Sept 26, 2019 – PADEP BAMR Grant Awarded to SFCG
Oct 1, 2019 – Kick-off Meeting at BAMR Ebensburg Office
May 11, 2020 – Agencies/Stakeholders/Contractors On-site Pre-Construction Meeting
January 18, 2021 – Start-up and Commissioning Begins
February 1, 2021 – Continuous Treatment Commences

## Slide 6
Gladden Discharge flowing from an open Mine Shaft

## Slide 7
The Gladden Discharge flows from the abandoned Montour No. 2 underground coal mine operated by the former Pittsburgh Coal Company and abandoned circa 1920
The discharge dumps on average more than 900 gallons (750 – 1,500 gpm) of iron-laden (90 – 130 mg/liter) water into Millers Run every minute (1.3 million gallons per day)
The Gladden AMD Discharge – Chartiers Creek Watershed

## Slide 8
Gladden Discharge Channel and Flow Measuring Weir

## Slide 9
Gladden Discharge Flowing into Millers Run

## Slide 10
Gladden Discharge Flowing into Millers Run

## Slide 11
According to watershed studies completed by the local conservation groups in conjunction with PA-DEP, the Gladden discharge is responsible for 40% of the iron loading and 50% of the acidity loading to Chartiers Creek
Within a half-mile from where the Gladden Discharge enters Millers Run, it changes from a clear stream with trout to an orange stream with virtually no life
The Gladden AMD Discharge – Chartiers Creek Watershed

## Slide 12
Gladden Discharge into Millers Run and Millers Run into Chartiers Creek
Raw Discharge: pH=6, Fe 100 ppm
Flows: Avg=750 gpm, 1,470 gpm max
Draining 5,500 acres of Mine Workings
1,500 acres of Mine Pool

## Slide 13
Millers Run then flows into Chartiers Creek degrading the stream quality to a point where it can support almost no aquatic life
Chartiers Creek, located partially in Washington and Allegheny Counties, flows into the Ohio River just a few miles downstream from the confluence of the Allegheny and Monongahela Rivers where the Ohio River begins in downtown Pittsburgh
The Gladden AMD Discharge – Chartiers Creek Watershed

## Slide 14
Aerial View of the Confluence of Millers Run and Chartiers Creek

## Slide 15: Chartiers Creek Watershed
Gladden Discharge

## Slide 16
Millers Run above AMD Impacts

## Slide 17
Millers Run above AMD Impacts

## Slide 18
Millers Run below AMD Impacts

## Slide 19
The Solution: Relocate and Treat the Mine Discharge at a New Mine Drainage Treatment Facility

## Slide 20: Treatment Plant Design
A 2.2 million gallons per day (MGD) treatment plant was designed to treat the existing Gladden discharge.
The Gladden AMD Treatment Facility is the first facility in PA that was designed from inception to be a Hydrogen Peroxide treatment plant.
The plant includes two pumping stations to extract the AMD water from the mine pool and bring it to the surface for treatment.
The treatment includes oxidation using industrial grade (50%) hydrogen peroxide addition, polymer addition to form solid precipitates, solids recirculation for enhanced flocculation, and a clarifier and settling/polishing pond to remove the precipitated metals and solids from the water.
The treated water is discharged to Millers Run, and the sludge is pumped to a portion of the mine that is not hydrologically connected for disposal.

## Slide 21: Treatment Plant Components
2 submersible turbine pumps rated at approximately 1,200 gpm located at a point in the mine to achieve a maximum drawdown elevation
A combination pre-aeration, reaction polymer slow mix tank with a design capacity of 1,600 gpm
A back-up NaOH chemical addition automated dosing system (only if needed)
A 5,600-gallon reserve capacity automated hydrogen peroxide dosing system
An emulsion polymer system
An 65-foot diameter clarifier, 1,600 gpm design capacity
A polishing pond with service water system
Redundant sludge boreholes and pumping systems
A main control building with an office, lab, and restroom

## Slide 22
System Process Flow Diagram

## Slide 23
Treatment Plant
Farmers Market
Rt. 50
Sludge Disposal
AMD Extraction Wells
Millers Run

## Slide 24
Treatment Plant and Sludge Disposal Line Layout over Mine Workings

## Slide 25
Civil Site Development – May 18, 2020
Initiation of Project Construction

## Slide 26
Civil Site Development – June 8, 2020

## Slide 27
Civil Site Development – June 12, 2020

## Slide 28
Civil Site Development – June 22, 2020

## Slide 29
Foundation Work Started – July 10, 2020

## Slide 30
Masking and Social Distancing Safety Protocols were Necessary as a Result of the COVID-19 Pandemic

## Slide 31
Foundation Work for Clarifier and Reaction Tank – July 23, 2020

## Slide 32
Site Construction – July 28, 2020

## Slide 33
Steel Reinforcement for the Clarifier Base – August 3, 2020

## Slide 34
Concrete Pour for the Clarifier Base – August 5, 2020

## Slide 35
Pouring the Foundation for the Clarifier – August 5, 2020

## Slide 36
Polishing Pond and Outlet Flow Control Structure Construction

## Slide 37
Clarifier Tank Walls and Control Building Foundation Progressing – August 19, 2020

## Slide 38
Clarifier:
WesTech Engineering LLC
65-ft. Diameter Conventional Clarifier with Sludge Recirculation

## Slide 39
Aerial View of Site Under Construction – August 25, 2020

## Slide 40
Installation of the Reaction Tank – August 26, 2020

## Slide 41
Reaction Tank:
Purestream Inc.
Dimensions: 62’ x 12’ with
3 Compartments

## Slide 42
Clarifier Tank Shell Completed – September 6, 2020

## Slide 43
Property Owner and Contractor John Kosky Watches an Early Morning Concrete Pour – September 14, 2020

## Slide 44
Control Building Construction – September 16, 2020

## Slide 45
Peroxide Building Construction – November 4, 2020

## Slide 46
Plant Construction – November 4, 2020

## Slide 47
Plant Construction – November 4, 2020

## Slide 48
Control Building Construction – October 6, 2020
Rhino Steel Building (74’ 6” x 48’ 4” x 20’)
Electrical Controls and MCC
Lab/Office and Restroom
Caustic Tank and Mixing
Polymer System
Sludge Disposal and Re-Circulation Pumps
Service Water and Sump Pumps

## Slide 49
Treatment Facility – January 8, 2021

## Slide 50
Installation of Sludge Line

## Slide 51
Sludge Line Corridor Seeded and Mulched

## Slide 52
Gladden AMD Treatment Facility Completed and Operating – March 22, 2021

## Slide 53
Treatment Plant Operations Center/ Office in the Control Building

## Slide 54
Caustic Soda Tank with Spill Containment in
Control Building – January 8, 2021

## Slide 55
Sodium Hydroxide Tank with Spill Containment in
Control Building – August 13, 2021

## Slide 56
Polymer Feed Pumps

## Slide 57
Hydrogen Peroxide Tank with Spill Containment in the Hydrogen Peroxide Building

## Slide 58
Sludge Pumps in Control Building

## Slide 59
65-ft. Conventional Clarifier

## Slide 60
Clarifier Rake Assemby

## Slide 61
Clarifier Superstructure and Catwalk

## Slide 62
Polymer Slow Mix Portion of the Reaction Tank

## Slide 63
Mixers on Top of Reaction Tank

## Slide 64
Mixer on Top of Reaction Tank

## Slide 65
350,000 Gallon Clarification Tank

## Slide 67
The Gladden AMD Treatment Facility has been removing ~1,050 lbs. of Iron every day which would have been discharging into Millers Run

## Slide 68: Iron Settleability Test to Determine Sludge Settling Rate and Polymer Dosing Rate
Special Thanks to:
Rich Beam, OSMRE / Former PaDEP
Brent Means, OSMRE
Joe Pehur, AMD Industries

## Slide 70
Completed and Operating Gladden AMD Treatment Facility – March 19, 2021

## Slide 71
Gladden Discharge After Plant Start Up – March 23, 2021

## Slide 72
Millers Run Near Cuddy PA 2/24/21 (4 Weeks after Startup)

## Slide 73
Before Treatment
After Treatment

## Slide 74
Aerial View Before Treatment
Aerial View After Treatment
The Gladden Treatment Facility is Restoring 4 Miles of Millers Run and 4 Miles of Chartiers Creek

## Slide 75
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony

## Slide 76
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony
Congressman Conor Lamb

## Slide 77
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony
Tetra Tech’s Tom Gray

## Slide 78
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony
SFCG’s Steve Frank and Tetra Tech’s Farley Wood

## Slide 79
South Fayette Conservation Board Members
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony

## Slide 80
April 27, 2021 – Gladden Project Dedication and Ribbon Cutting Ceremony
Project Partner Representatives from SFCG, Tetra Tech, PA DEP, OSMRE, and PFBC

## Slide 81: The Final Product – The Gladden AMD Treatment Plant

## Slide 82
The Final Product – Millers Run Near Cuddy Post Office

## Slide 83
The Final Product – Millers Run at its Confluence with Chartiers Creek

## Slide 84: Project Funding
The Gladden AMD Treatment Project cost just over $13 million.
The funding for the project came from two primary sources:
  The AMD abatement and treatment program (AMD Set-Aside Program) authorized in the Surface Mining Control and Reclamation Act (SMCRA).
  The federal Office of Surface Mining Reclamation and Enforcement’s (OSMRE’s) AML Pilot Program, now referred to as the federal Abandoned Mine Land Economic Revitalization (AMLER) Program.
The AMLER Program specifically targets abandoned mine cleanup projects that are linked to local community and economic development goals.
Additional funding through Growing Greener has been awarded to support long-term operation and maintenance of this treatment system by providing 2 years of additional O&M funding. Current annual cost is $300,000.

## Slide 85: Project Grant and Contracting Mechanisms
The entire Gladden AMD Treatment Facility design and construction methodology was facilitated by a PA DEP BAMR grant and contracting process awarded to the local project sponsor, the South Fayette Conservation Group (SFCG).
SFCG, through a competitive bid process, retained design engineering services, construction contractors and plant operators through the PA DEP BAMR reimbursement grant process.
This methodology resulted in the treatment plant being designed, constructed, and placed into operation within only a 14-month time frame, despite the fact that construction occurred during the height of the global Covid-19 pandemic.

## Slide 86: Economic and Community Benefits
The Gladden AMD Active Treatment Plant is restoring 4 miles of Millers Run and will be instrumental in restoring 14 miles of Chartiers Creek to the confluence with the Ohio River.
Millers Run is on the PA Fish Commission stocking list upstream of the Gladden Discharge. The plant will enable the fish to migrate down into the remaining 4 miles of Millers Run.
This section of stream flows past Morgan Park and through the Newberry Market development, both of which provide good access points for fishing.
The Newbury development is 300-acre site of which about 200 acres is being developed into two residential communities and the remaining 100 acres is being developed into a mixed-use commercial retail development to include a pedestrian friendly main street with shops, restaurants, outdoor plazas, a hotel, grocery store and retail tenants.

## Slide 87: Economic and Community Benefits
The restoration of this section of Millers Run provides an aesthetically pleasing stream for this development and existing residential areas and also provides a stream with a high potential for recreational visitation.
Chartiers Creek flows past Meyer & Middleton Park, which also provides fishing/recreational access for the stream.
Chartiers Creek is also a common place for canoes and kayaks, with seven boat launches along its banks between Canonsburg Lake and the Ohio River. Individuals and organized groups travel the waters on a regular basis.
The Chartiers Creek watershed is experiencing an economic boom and having clean streams and a clean environment visible to the public are an essential part of a vibrant community.

## Slide 88
The Gladden AMD Treatment Facility Project was the Recipient of a 2022 Pennsylvania Governor’s Award for Environmental Excellence
Staff from Tetra Tech and South Fayette Conservation Group at the April 26, 2022 Awards Ceremony

## Slide 89: OUR PARTNERS
OSMRE
Pennsylvania DEP-BAMR
South Fayette Conservation Group
John Kosky Contacting

## Slide 90: OUR PARTNERS
Chapman Corporation
Ligonier Construction
Infinity Drilling

## Slide 91: CONTACTS:
  Heather Trexler, P.G.
    Email: Heather.Trexler@tetratech.com
    Cell: (412) 944-8106
  Eric Cavazza, P.E.
    Email: Eric.Cavazza@tetratech.com
    Cell: (412) 522-9764
  Tom Gray, P.E.
    Email: Thomas.Gray@tetratech.com
    Cell: (412) 526–5095